## Slide 1: Canton, NC WWTP Transition Plan and Recommendations

## Slide 2: WWTP Transition Plan
Phase I
  1A Initial Outage Preparation(prior to beginning of mill outage)
    PH control
    Surge Volume—using Primary Clarifier
    Chemicals required
      Sulfuric Acid, C02, Coagulants/Polymers , Supplemental Nutrients
  1B Beginning of Mill Outage (Similar to shutting down for annual outage)
    Timeframe (Weeks)
    Continue to run WWTP as an Activated Sludge System at full capacity
    Monitor flow, BOD/surrogate loading, and Food/Microorganism (F/M) ratio
    Phase 1 to end when flow/loading/F/M reaches 50% of normal levels—Use rolling average numbers—3-5day rolling average

## Slide 3
AB or Digester
(2.3 MG)
AB or Digester
(2.3 MG)
Aeration Basin
(3.4 MG)
Aeration Basin
(3.4 MG)
#1
Primary Clarifier
(1.01 MG)
#2
Primary Clarifier
(3.47 MG)
#3
Primary Clarifier
(3.47 MG)
#4
Secondary Clarifier
(2.82 MG)
#5
Secondary Clarifier
(2.82 MG)
#6
Secondary Clarifier
(1.85 MG)
Flow
Splitting Station
Low
Lift
Pumps
Bar Screens
Grit Chamber
City Sewer
RAS
Belt Presses
Mill Wastewater
Primary Sludge
WAS
Phase I Initial Shutdown Activated Sludge Full Capacity

## Slide 4: WWTP Transition Plan
Phase II (Time frame-Months)
  Tank, vessel, mill, and piping clean-up
  Similar to tail end of annual outages
    Reduced flow and Loading
    F/M will be reduced
  Begin taking excess equipment off-line
    Primary Clarifiers
    Stop C02
    Secondary Clarifiers
    Take one of the two aeration trains out of service
    Continue to run activated sludge process
    Belt Presses
    Low lift pumps

## Slide 5
AB or Digester
Down
AB or Digester
(2.3 MG)
Aeration Basin
Down
Aeration Basin
(3.4 MG)
#1
Primary Clarifier
(1.01 MG)
#2
Primary Clarifier
(3.47 MG)
#3
Primary Clarifier
Storm Surge
(3.47 MG)
#4
Secondary Clarifier Emergency Use
(2.82 MG)
#5
Secondary Clarifier
(2.82 MG)
#6
Secondary Clarifier
(1.85 MG)
Flow
Splitting Station
Low
Lift
Pumps
Bar Screens
Grit Chamber
City Sewer
RAS
Belt Presses
Mill Wastewater
Primary Sludge
WAS
Phase II Partial Shutdown Activate Sludge

## Slide 6: WWTP Transition Plan
Phase III (Timeframe—Months)
  Phase III begins when mill flow/loading approaches zero
  Municipal flow only approximately 1 MGD except for storm flows
  Long Term End Game WWTP—Flow scheme
    Primary Treatment
      Grit chamber, Bar screen, Low lift pump/s as required, flow splitting station
    Primary Clarification
      #1 Primary Clarifier-1.01 MG
      #2 & #3 storm surge (6.9MG)
    Secondary Treatment
      One train in ASB(Aerated Stabilization Basin) once through system
        2.3 MG section aerated; 3.4 MG section final aeration and settling area

## Slide 7: WWTP Transition Plan
Phase III continued
  Secondary/tertiary Clarification
    Last part of aeration train (3.4 MG)
    #6 or #5 Clarifier
    #4 & #5 Out of service available for emergency use (9.6 MG)
      Storm surge or off-spec quality treated water
  Flow Measurement, Reaeration, and Discharge
    Flume—flow compliance
    Reaeration Cascade—O2 injection
    Final Discharge

## Slide 8
AB or Digester
Down
AB or Digester
(2.3 MG)
Aeration Basin
Down
Aeration/
Settling
(3.4 MG)
#1
Primary Clarifier
(1.01 MG)
#2
Primary Clarifier Storm Surge
(3.47 MG)
#3
Primary Clarifier
Storm Surge
(3.47 MG)
#4
Secondary Clarifier Emergency Use
(2.82 MG)
#5
Secondary Clarifier
Emergency Use
(2.82 MG)
#6
Secondary Clarifier
(1.85 MG)
Flow
Splitting Station
Low
Lift
Pumps
Bar Screens
Grit Chamber
City Sewer
Belt Presses
Primary Sludge
Phase III Municipal Flow ASB once through Operation
Leachate/ storm flow

## Slide 9: WWTP Transition Plan
Further Investigation/Data Needs
  O2 Addition Optimization
  City of Canton– WWTP data
    Industrial components of Canton wastewater
    Nitrogen and Ammonia content of Canton wastewater
    Normal and Maximum flows
  Landfill Leachate characterization
  Last Permit Renewal Priority Pollutant analysis
  Mill operator input on transition plan
  Treatability study to confirm needed residence time for ASB (once through) operation
  Sampling and analysis planned for the week of March 20.