## Sheet1
| Summary of Requirements for 40 CFR Part 63 Subpart JJJJJJ: NESHAP for Area Sources: Industrial, Commercial, and Institutional Boilers | [5 empty] | Summary of Requirements for 40 CFR Part 63 Subpart JJJJJJ: NESHAP for Area Sources: Industrial, Commercial, and Institutional Boilers
|  | Task 1 Submit Initial Notifications |  | Task 2 Comply with Work Practice Standards (§63.11201, Table 2) |  |  | Task 3 Meet Emission Limits |  |  | Task 4 | Task 5
Row | Subcategory | Submit Initial Notification of Applicability1 | Submit Initial Notification of Compliance Status2 | Minimize Startup/ Shutdown per Mfg. Procedures | Conduct Performance Tune-up2,3 | Conduct Energy Assessment | For this pollutant | Initial Compliance | Continuous Compliance | Record | Submit Other Notifications and Reports
| ALL Gas-Fired Boilers (ALL sizes, new or existing) | [5 empty] | ALL Gas-Fired Boilers (ALL sizes, new or existing)
1 | Gas | No | No | No | No | No | None |  |  | None | None
| Existing - Small (< 10MMBtu/hr) | [5 empty] | Existing - Small (< 10MMBtu/hr)
2 | All fuel types other than gas (biomass, coal, oil) | Yes, submit by 9/17/2011. §63.11225(a)(2) | Yes, submit by 7/19/2012. 63.11225(a)(4) | No | Yes, Biennial. First tune-up completed by 3/21/2012. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | No | None |  |  | Biennial compliance certification report (§63.11225(b)). Prepare first report by 3/1/2015. Subsequent reports prepared by March 1 of every other year. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6))
[10 empty] | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records on 5/20/2011. | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
Records of all submitted notifications (§63.11225(c)(1))
| Existing - Large (≥ 10MMBtu/hr) | [5 empty] | Existing - Large (≥ 10MMBtu/hr)
3 | Biomass | Yes, submit by 9/17/2011. §63.11225(a)(2) | Yes, submit by 7/19/2012 for tune-up. Re-submit by 7/19/2014 for energy assessment. 63.11225(a)(4) | No | Yes, Biennial. First tune-up completed by 3/21/2012. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | Yes, by 3/21/2014. (Table 2) | None |  |  | Biennial compliance certification report (§63.11225(b)). Prepare first report by 3/1/2015. Subsequent reports prepared by March 1 of every other year. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6)).
[10 empty] | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records on 5/20/2011. | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
Records of all submitted notifications (§63.11225(c)(1))
Energy Assessment Report (§63.11214(c)) should be completed by 3/21/2014.
4 | Oil | Yes, submit by 9/17/2011. §63.11225(a)(2) | Yes, submit by 7/19/2012 for tune-up. Re-submit by 7/19/2014 for energy assessment. 63.11225(a)(4) | No | Yes, Biennial. First tune-up completed by 3/21/2012. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | Yes, by 3/21/2014. (Table 2) | None |  |  | Biennial compliance certification report (§63.11225(b)). Prepare first report by 3/1/2015. Subsequent reports prepared by March 1 of every other year. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6))
[10 empty] | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records on 5/20/2011. | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
Records of all submitted notifications (§63.11225(c)(1))
Energy Assessment Report (§63.11214(c)) should be completed by 3/21/2014.
| Existing - Large (≥ 10MMBtu/hr) | [5 empty] | Existing - Large (≥ 10MMBtu/hr)
5 | Coal | Yes, submit by 9/17/2011. §63.11225(a)(2) | Yes . Submit within 60 days of conducting performance test for mercury and CO, or no later than 11/16/2014, whichever is earlier. Submit by 7/19/2014 for energy assessment. (§63.11225(a)(4)). Include a statement on Startup and Shutdown according to manufacturer specifications (§63.11223(c)) | Yes, beginning 3/21/2014. §63.11223(c) §63.11214(d) | No | Yes, by 3/21/2014. (Table 2) | Hg | Conduct performance (stack) test (§63.11212, Table 4, and 63.7(c), (d), (f)) by 9/17/2014. | Triennial stack test (§63.11220(a) and §63.11212), no more than 37 months after previous test. | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records in March 2013. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
[8 empty] | OR |  | Records of all submitted notifications (§63.11225(c)(1)) | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
[8 empty] | Conduct fuel analysis (63.11213, Table 5 and 63.11211(c)) by 9/17/2014. | If Hg limit compliance demonstrated based on fuel analysis, conduct fuel analysis for each fuel type burned monthly (§63.11213 and §63.11220(e)) | Energy Assessment Report (§63.11214(c)) should be completed by 3/21/2014. | Deviations from emission limits and corrective actions taken during reporting period (§63.11225 (b)(3)).5 Submit by March 15 of each calendar year where deviations occurred.
[8 empty] | Establish operating limits (§63.11222, Table 6 and 63.11211(b)) by 9/17/2014. | Operate monitoring systems and collect data at all required intervals (§63.11221 and Table 7) including fuel mercury content and relevant control device monitoring systems. | For sources demonstrating compliance with fuel analysis, records of all calculation and supporting documentation to demonstrate compliance with emission limits (§63.11225(c)(3))
[8 empty] | Conduct CMS performance evaluations (§63.11224)4 by 9/17/2014. |  | Records of type and amount of all fuels burned in each boiler during reporting period (§63.11222(a)) | Notification of affirmative defense within two business days of malfunction (§63.11226(b)
[7 empty] | CO | Conduct performance (stack) test (§63.11212 and Table 4) by 9/17/2014. | Triennial stack test (§63.11212) | Records of the each boiler or control device malfunction occurrence and duration and actions taken to minimize emissions during malfunctions (§63.11225(c)(4)-(5))
[8 empty] | Establish operating limits (§63.11222, Table 6 and §63.11211(b)) by 9/17/2014. |  | Records of monitoring data and maintenance (§63.11225(c)(6)) | Root cause analysis report of the malfunction within 45 days of the exceedance of the standard (§63.11226(b))
[8 empty] | Install oxygen monitor (§63.11224(a)) by 9/17/2014. |  | Site-specific test plan shall be prepared before each stack test (§63.11212(a), §63.7(c))6
[8 empty] | Establish operating limits (§63.11222 and 63.11211(b)) by 9/17/2014. | Operate monitoring systems and collect data at all required intervals (§63.11221 and Table 7). | Annual compliance certification report (§63.11225(b))5,6 Prepare first report by 3/1/2015. Thereafter, by March 1 of each calendar year. | Submit results of mercury test data to EPA's Central Data Exchange using the ERT <http://www.epa.gov/ttnchie1/ert/ert_tool.html> (§63. 11225(e)) within 60 days of completing each performance test.
[8 empty] | Conduct CMS performance evaluations (§63.11224) by 9/17/2014. |  | Site-specific monitoring plan shall be prepared 60 days before CMS performance evaluation for each CMS (§63.11205(c)(1) through (3))6
| New - Small (< 10MMBtu/hr) | [5 empty] | New - Small (< 10MMBtu/hr)
6 | All fuel types other than gas (biomass, coal, oil) | Yes, submit by 9/17/2011 or within 120 days after startup, whichever is later. §63.11225(a)(2) | Yes, submit by 9/17/2011 or within 120 days of startup, whichever is later. §63.11225(a)(4) | No | Yes, Biennial. First tune-up completed by 5/20/2011 or upon start-up of the boiler, whichever is later. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | No | None |  |  | Biennial compliance certification report (§63.11225(b)). Prepare by 3/1/2012 or on March 1 of the year immediately following start-up of the boiler. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6))
[10 empty] | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records upon start-up of the boiler. | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
Records of all submitted notifications (§63.11225(c)(1))
| New - Large (≥ 10MMBtu/hr) | [5 empty] | New - Large (≥ 10MMBtu/hr)
7 | Coal | Yes, submit by 9/17/2011 or within 120 days after startup, whichever is later. §63.11225(a)(2) | Yes, submit within 60 days of completing the performance test. (§63.11225(a)(4)). Include a statement on Startup and Shutdown according to manufacturer specifications (§63.11223(c)) | Yes, beginning 5/20/2011 or upon start-up of the boiler. §63.11223(c) §63.11214(d) | No | No | Hg | Conduct performance (stack) test (§63.11212, Table 4, and 63.7(c), (d), (f)) within 180 days of startup, or by 9/17/2011, whichever is later. | Triennial stack test (§63.11220(a) and §63.11212), no more than 37 months after previous test. | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records upon start-up of the boiler. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
[8 empty] | OR |  | Records of all submitted notifications (§63.11225(c)(1)) | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
[8 empty] | Conduct fuel analysis (§63.11213, Table 5 and §63.11211(c)) within 180 days of startup or by 9/17/2011, whichever is later. | If Hg limit compliance demonstrated based on fuel analysis, conduct fuel analysis for each fuel type burned monthly (§63.11213 and §63.11220(e)) | For sources demonstrating compliance with fuel analysis, records of all calculation and supporting documentation to demonstrate compliance with emission limits (§63.11225(c)(3))
[8 empty] | Establish operating limits (§63.11222, Table 6 and §63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later. | Operate monitoring systems and collect data at all required intervals (§63.11221 and Table 7) including fuel mercury content and relevant control device monitoring systems. |  | Deviations from emission limits and corrective actions taken during reporting period (§63.11225 (b)(3)).5 Submit by March 15 of each calendar year where deviations occurred.
[8 empty] | Conduct CMS performance evaluations (§63.11224)4 with 180 days of startup or by 9/17/2011, whichever is later. |  | Records of type and amount of all fuels burned in each boiler during reporting period (§63.11222(a))
[7 empty] | CO | Conduct performance (stack) test (§63.11212 and Table 4) within 180 days of startup or by 9/17/2011, whichever is later. | Triennial stack test (§63.11212), no more than 37 months after previous test. | Records of the each boiler or control device malfunction occurrence and duration and actions taken to minimize emissions during malfunctions (§63.11225(c)(4)-(5)) | Notification of affirmative defense within two business days of malfunction (§63.11226(b)
Establish operating limits (§63.11222, Table 6 and §63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later.
[8 empty] | Install oxygen monitor (§63.11224(a)) within 180 days of startup or by 9/17/2011, whichever is later. |  | Records of monitoring data and maintenance (§63.11225(c)(6)) | Root cause analysis report of the malfunction within 45 days of the exceedance of the standard (§63.11226(b))
[8 empty] | Establish operating limits (§63.11222 and 63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later. | Operate monitoring systems and collect data at all required intervals (§63.11221 and Table 7). | Annual compliance certification report (§63.11225(b))5,6. Prepare first report by 3/1/2012 (or on March 1 of the calendar year immediately following start-up of the boiler). Subsequent reports prepared by March 1 of the next calendar year.
[8 empty] | Conduct CMS performance evaluations (§63.11224) within 180 days of startup or by 9/17/2011, whichever is later. |  |  | Submit results of mercury, CO and PM test data to EPA's Central Data Exchange using the ERT <http://www.epa.gov/ttnchie1/ert/ert_tool.html> (§63. 11225(e)) within 60 days of completing each performance test.
[7 empty] | PM | Conduct performance (stack) test (§63.11212 and Table 4) within 180 days of startup or by 9/17/2011, whichever is later. | Triennial stack test (§63.11212), no more than 37 months after previous test. | Site-specific monitoring plan shall be prepared 60 days before CMS performance evaluation for each CMS (§63.11205(c)(1) through (3))6
[8 empty] | Establish operating limits (§63.11222 and 63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later. |  | Site-specific test plan shall be prepared before each stack test (§63.11212(a), §63.7(c))6
[8 empty] | Conduct CMS performance evaluations (§63.11224) within 180 days of startup or by 9/17/2011, whichever is later. | Monitor parameters and collect data (§63.11221)
| New - Large (≥ 10MMBtu/hr) | [5 empty] | New - Large (≥ 10MMBtu/hr)
8 | Biomass | Yes, submit by 9/17/2011 or within 120 days after startup, whichever is later. §63.11225(a)(2) | The notification for compliance with the PM emission limits must be submitted within 60 days of completing the performance test and you can resubmit a notification for the tune-up (§63.11225(a)(4)). If this notification does not include the tune-up, you can re-submit a notification for the tune-up by 9/17/2011, or within 120 days of startup, whichever is later. Include a statement on Startup and Shutdown according to manufacturer specifications (§63.11223(c)) | Yes, beginning 5/20/2011 or upon start-up of the boiler. §63.11223(c) §63.11214(d) | Yes, Biennial. First tune-up completed by 5/20/2011 or upon start-up of the boiler, whichever is later. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | No | PM | Conduct performance (stack) test (§63.11212 and Table 4) within 180 days of startup or by 9/17/2011, whichever is later. | Triennial stack test (§63.11212) no more than 37 months after previous test. | Annual compliance certification report (§63.11225(b))5,6 Prepare first report by 3/1/2012 (or on March 1 of the calendar year immediately following start-up of the boiler). Subsequent reports prepared by March 1 of the next calendar year. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
[10 empty] | Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6)) | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
[8 empty] | Establish operating limits (§63.11222 and 63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later. |  | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records upon start-up of the boiler. | Deviations from emission limits and corrective actions taken during reporting period (§63.11225 (b)(3)).5
[8 empty] | Conduct CMS performance evaluations (§63.11224) within 180 days of startup or by 9/17/2011, whichever is later. | Monitor parameters and collect data §63.11221 | Records of all submitted notifications (§63.11225(c)(1))
[10 empty] | Records of the each boiler or control device malfunction occurrence and duration and actions taken to minimize emissions during malfunctions (§63.11225(c)(4)-(5)) | Notification of affirmative defense within two business days of malfunction (§63.11226(b)
[10 empty] | Records of monitoring data and maintenance (§63.11225(c)(6) | Root cause analysis report of the malfunction within 45 days of the exceedance of the standard (§63.11226(b))
[10 empty] | Site-specific monitoring plan shall be prepared 60 days before CMS performance evaluation for each CMS (§63.11205(c)(1) through (3))6 | Submit results of PM test data to EPA's Central Data Exchange using the ERT <http://www.epa.gov/ttnchie1/ert/ert_tool.html> (§63. 11225(e)) within 60 days of completing each performance test.
Site-specific test plan shall be prepared before each stack test (§63.11212(a), §63.7(c))6
| New - Large (≥ 10MMBtu/hr) | [5 empty] | New - Large (≥ 10MMBtu/hr)
9 | Oil | Yes, submit by 9/17/2011 or within 120 days after startup, whichever is later. §63.11225(a)(2) | The notification for compliance with the PM emission limits must be submitted within 60 days of completing the performance test and you can resubmit a notification for the tune-up (§63.11225(a)(4)). If this notification does not include the tune-up, you can re-submit a notification for the tune-up by 9/17/2011, or within 120 days of startup, whichever is later. Include a statement on Startup and Shutdown according to manufacturer specifications (§63.11223(c)) | Yes, beginning 5/20/2011 or upon start-up of the boiler. §63.11223(c) §63.11214(d) | Yes, Biennial. First tune-up completed by 5/20/2011 or upon start-up of the boiler, whichever is later. Subsequent tune-ups should be completed no later than 25 months after the previous tune-up. §63.11223(b) | No | PM | Conduct performance (stack) test (§63.11212 and Table 4) within 180 days of startup or by 9/17/2011, whichever is later. | Triennial stack test (§63.11212) no more than 37 months after previous test. | Annual compliance certification report (§63.11225(b))5,6 Prepare first report by 3/1/2012 (or on March 1 of the calendar year immediately following start-up of the boiler). Subsequent reports prepared by March 1 of the next calendar year. | Notification to combust solid waste (§63.11225(f)). Submit 30 days prior to combusting solid waste.
[10 empty] | Records of dates and procedures for each boiler tune up (§63.11225(c)(2)(i) and §63.11223(b)(6)) | Notification of fuel or subcategory switching (§63.11225(g)). Submit 30 days prior to switching fuels.
[8 empty] | Establish operating limits (§63.11222 and 63.11211(b)) within 180 days of startup or by 9/17/2011, whichever is later. |  | Records of fuel use and non-waste determinations (§63.11225(c)(2)(ii)). You should begin keeping fuel records upon start-up of the boiler. | Deviations from emission limits and corrective actions taken during reporting period (§63.11225 (b)(3)).5
[8 empty] | Conduct CMS performance evaluations (§63.11224) within 180 days of startup or by 9/17/2011, whichever is later. | Monitor parameters and collect data §63.11221 | Records of all submitted notifications (§63.11225(c)(1))
[10 empty] | Records of the each boiler or control device malfunction occurrence and duration and actions taken to minimize emissions during malfunctions (§63.11225(c)(4)-(5)) | Notification of affirmative defense within two business days of malfunction (§63.11226(b)
[10 empty] | Records of monitoring data and maintenance (§63.11225(c)(6)) | Root cause analysis report of the malfunction within 45 days of the exceedance of the standard (§63.11226(b))
[10 empty] | Site-specific monitoring plan shall be prepared 60 days before CMS performance evaluation for each CMS (§63.11205(c)(1) through (3))6 | Submit results of PM test data to EPA's Central Data Exchange using the ERT <http://www.epa.gov/ttnchie1/ert/ert_tool.html> (§63. 11225(e)) within 60 days of completing each performance test.
Site-specific test plan shall be prepared before each stack test (§63.11212(a), §63.7(c))6
[7 empty] | 1 | Initial Notification of Applicability. National Emissions Standards for Hazardous Air Pollutants: Industrial, Commercial, and Institutional Boilers Area Sources (40 CFR Part 63 Subpart JJJJJJ). March 31, 2011. Available online at: <http://www.epa.gov/airtoxics/boiler/boilerpg.html>
[7 empty] | 2 | Initial Notification of Compliance Status for Boilers Subject to Tune-ups - Area Sources. National Emissions Standards for Hazardous Air Pollutants: Industrial, Commercial, and Institutional Boilers Area Sources (40 CFR Part 63 Subpart JJJJJJ). April 21, 2011. Available online at: <http://www.epa.gov/airtoxics/boiler/boilerpg.html>
[7 empty] | 3 | Tune-up Guidance and Example Recordkeeping Form-Area Sources. National Emissions Standards for Hazardous Air Pollutants: Industrial, Commercial, and Institutional Boilers Area Sources (40 CFR Part 63 Subpart JJJJJJ). April 21, 2011. Available online at: <http://www.epa.gov/airtoxics/boiler/boilerpg.html>
[7 empty] | 4 | Only for source that petitions for an alternative monitoring parameters under §63.8. Mercury CEMS is not required under this rule.
[7 empty] | 5 | If deviations occur during the reporting period, you must submit the entire contents of the annual compliance certification report ( §63.11225(b) by March 15 of the calendar year immediately following the reporting period.
[7 empty] | 6 | These items must be prepared and kept on-site unless your delegated authority requests these items to be submitted.

## progression
Assume this boiler isn't required to have a permit under section 3005 of the Solid Waste Disposal Act or covered by subpart EEE of this part (e.g., hazardous waste boilers) [exempt under § 63.11195(c)]
1. Own or operate a boiler to provide steam, hot water, and/or electricity (a collection of all existing boilers within a subcategory or each new or reconstructed boiler)
2. Located at, or is part of, an area source of HAP
2A. Not an affected source if boilers that are subject to another standard under 40 CFR part 63 or to a standard developed under CAA section 129.
2B. Not used specifically for R&D (does not include boilers that solely or primarily provide steam (or heat) to a process or for heating at a R&D facility).
2C. Not a hot water heater (i.e., closed vessel with a capacity less than or equal to 120 U.S. gallons in which water is heated by combustion of gaseous or liquid fuel; water shall not be withdrawn at pressures exceeding 160 psig, including the apparatus to prevent water temperatures from exceeding 210 degrees Fahrenheit).
missing waste heat and haz waste should go here |  | 2D. Not a control device to comply with another subpart of this part; at least 50 percent of the heat input to the boiler is provided by by a gas stream that is regulated under another subpart.
3. Is your boiler gaseous-fired (i.e., not combination of solid fuels and burns liquid fuel only for periodic testing not to exceede 48-hrs/yr).
GO TO ROW # 1
4. Existing source if you commenced construction or reconstruction on or before June 4, 2010.
4A.Is your boilers designed heat input capacity LESS than 10 MMBtu/hr?
GO TO ROW # 2
4B. If your boiler burns at least 15 percent biomass on a total fuel annual heat input basis, the unit is in the biomass subcategory.
GO TO ROW # 3
4C. If your boiler burns any solid fossil fuel and no more than 15 percent biomass on a total fuel annual heat input basis, the boiler is in the coal subcategory.
IF NO, GO TO ROW # 4 (i.e., boiler burns any liquid fuel and is not in either the coal or the biomass subcategory, the unit is in the oil subcategory, except if the unit burns oil only during periods of gas curtailment)
IF YES, GO TO ROW # 5
5. New source if you commenced construction or reconstruction OR switched from natural gas fuel to solid fossil fuel, biomass, or liquid fuel after June 4, 2010.
5A. Is your boilers designed heat input capacity LESS than 10 MMBtu/hr?
GO TO ROW # 6
5B. If your boiler burns any solid fossil fuel and no more than 15 percent biomass on a total fuel annual heat input basis, the boiler is in the coal subcategory.
GO TO ROW # 8
5C. If your boiler burns at least 15 percent biomass on a total fuel annual heat input basis, the unit is in the biomass subcategory.
IF YES, GO TO ROW # 7
IF NO, GO TO ROW # 9 (i.e., boiler burns any liquid fuel and is not in either the coal or the biomass subcategory, the unit is in the oil subcategory, except if the unit burns oil only during periods of gas curtailment)
6/1/11 - ARS edits in red