VAR Option 3 Documentation Requirements Policy

(NC WW/GW LCB 06/08/2022)

The VAR: Option 3 method (See Section 8.4 on page 60 and Appendix D, Section 3 on page 130) requires that the sludge be sampled every week for five successive weeks.  There are also daily requirements.

Initial documentation must include:

•	Dimensions and volume of the digester

•	Initial percent solids value;  Must be ≤ 2% at the start of the test

•	Method used for Volatile Solids determination

•	Confirmation that the oil and particle free air was supplied to the bottom of the digester through a porous stone at a rate sufficient to thoroughly mix the sewage sludge

•	Dissolved oxygen reading;  Reading must be ≥ 2 mg/L to be acceptable.  If it is not, increase air flow until it is.

Daily documentation must include:

•	Confirmation that water loss from the digester is made up every day with distilled water;  That can be documented using a check box

•	Confirmation that solids that adhere to the walls above and below the water line are scraped off and dispersed back into the sludge;  That can be documented using a check box

•	Digestion temperature (i.e., 20 °C).  The method also states that if the room temperature is maintained at about 22 °C, that evaporation of the water from the digester will cool the sludge to about 20 °C.

Weekly documentation must include:

•	Date and time of sample collection

•	Dissolved oxygen reading at the time of collection.  Reading must be ≥ 2 mg/L to be acceptable.  This would also include proper documentation of the meter calibration.  If DO is not ≥ 2 mg/L , increase air flow until it is and begin daily monitoring of DO until 3 consecutive days of values ≥ 2 mg/L are obtained.  Weekly measure may resume after that.

•	Total Solids value (included along with this would be all required documentation for that test (e.g., oven temperature, time in and out of oven, balance weight-check, etc.)

•	Volatile Solids value (included along with this would be all required documentation for that test (e.g., oven temperature, time in and out of oven, balance weight-check, etc.)

Final documentation must include:

•	Volatile Solids reduction value and calculation