| UST-6D/23A Page 1 |  | Triennial UST Spill Bucket Integrity Testing (Hydrostatic/Vacuum Test) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - If any periodic test fails, a suspected release report must be submitted on a UST-17A form, UST Suspected Release 24 Hour Notice. The suspected release must be investigated, in accordance with 15A NCAC 2N .0603, and defective equipment repaired or replaced in accordance with 15A NCAC 2N .0404/.0900. Results of the investigation must be submitted on a UST-17B form, UST Suspected Release 7 Day Notice. - The primary containment and interstitial space of the spill bucket shall be tested in accordance with the manufacturer’s written guidelines, PEI/RP100 “Recommended Practices for Installation of Underground Liquid Storage Systems” and/or PEI/RP1200 “Recommended Practices for the Testing and Verification of Spill, Overfill, Leak Detection and Secondary Containment Equipment at UST Facilities.” - The primary and secondary walls are both considered to be tested at the same time if vacuum is used to test the interstice. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UST FACILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Owner / Operator Name |  |  |  | Facility Name |  |  |  |  |  |  |  |  | Facility ID#: |  |  |  |  |  |  |  |  |  |
| Facility Street Address |  |  |  | Facility City |  |  |  |  |  |  |  |  | County |  |  |  |  |  |  |  |  |  |
| TESTING CONTRACTOR INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company Name |  |  |  | Phone |  |  |  |  |  |  | E-mail Address |  |  |  |  |  |  |  |  |  |  |  |
|  | I certify, under penalty of law, that the testing data provided on this form documents the UST system equipment was tested in accordance with the manufacturer’s guidelines and the applicable national industry standards listed in 15A NCAC 2N .406 and/or 15A NCAC 2N .0900. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Print Name of person conducting test |  |  |  |  |  |  | Signature of person conducting test |  |  |  |  |  |  |  |  | Test Date |  |  |  |  |  |
| Identify Spill Bucket (By Tank Number, Stored Product, etc.) |  |  | Tank # |  |  | Tank # |  |  | Tank # |  |  | Tank # |  |  |  |  |  | Tank # |  |  |  |  |
| Tank Size |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Product |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Indicate units for all measurements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bucket Manufacturer/Model |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bucket Depth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Construction |  |  | SW DW |  |  | SW DW |  |  | SW DW |  |  | SW DW |  |  |  |  |  | SW DW |  |  |  |  |
| Bucket Installation Type |  |  | Direct Bury Direct Bury w/Liner Containment sump |  |  | Direct Bury Direct Bury w/Liner Containment sump |  |  | Direct Bury Direct Bury w/Liner Containment sump |  |  | Direct Bury Direct Bury w/Liner Containment sump |  |  |  |  |  | Direct Bury Direct Bury w/Liner Containment sump |  |  |  |  |
| Test Type |  |  | Hydrostatic Vacuum |  |  | Hydrostatic Vacuum |  |  | Hydrostatic Vacuum |  |  | Hydrostatic Vacuum |  |  |  |  |  | Hydrostatic Vacuum |  |  |  |  |
| Liquid and debris removed from spill bucket? |  |  | Yes No |  |  | Yes No |  |  | Yes No |  |  | Yes No |  |  |  |  |  | Yes No |  |  |  |  |
| Visual inspection (No cracks, loose parts or separation of the bucket from fill pipe.) |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail |  |  |  |  |  | Pass Fail |  |  |  |  |
| Tank riser cap included in test? |  |  | Yes No N/A |  |  | Yes No N/A |  |  | Yes No N/A |  |  | Yes No N/A |  |  |  |  |  | Yes No N/A |  |  |  |  |
| Drain valve included in test? |  |  | Yes No N/A |  |  | Yes No N/A |  |  | Yes No N/A |  |  | Yes No N/A |  |  |  |  |  | Yes No N/A |  |  |  |  |
| Wait time between applying vacuum/water and start of test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Primary Section Test Hydrostatic: Water level must be within 1.5 inches of top of bucket Vacuum: Apply vacuum of 30 inches WC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin I End Test Time |  |  | I |  |  | I |  |  | I |  |  | I |  |  |  |  |  | I |  |  |  |  |
| Begin I End Reading |  |  | I |  |  | I |  |  | I |  |  | I |  |  |  |  |  | I |  |  |  |  |
| Secondary Interstice Test Vacuum: Apply vacuum of 15 inches WC |  |  |  |  |  |  |  |  |  | Gauge range (with units): |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin I End Test Time |  |  | I |  |  | I |  |  | I |  |  | I |  |  |  |  |  | I |  |  |  |  |
| Begin I End Reading |  |  | I |  |  | I |  |  | I |  |  | I |  |  |  |  |  | I |  |  |  |  |
| Pass/fail criteria: Must pass visual inspection. Pass if: Hydrostatic: Water level drop of less than 1/8 inch in 1 hour; Vacuum single-walled only: Maintain at least 26 inches water column for 1 minute; Vacuum double-walled: Maintain at least 12 inches water column for 1 minute |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Results |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail |  |  |  |  |  | Pass Fail |  |  |  |  |
| Comments – (include information on repairs made prior to testing, and recommended follow-up for failed tests) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date next Spill Bucket integrity test due (required every 3 years) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NORTH CAROLINA DEPARTMENT OF ENVIRONMENTAL QUALITY, DIVISION OF WASTE MANAGEMENT, UST SECTION 1646 MAIL SERVICE CENTER, RALEIGH, NC 27699-1646 PHONE (919) 707-8171 FAX (919) 715-1117 http://www.wastenotnc.org/ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11/2022 |  |  |

| UST-6D/23A Page 2 |  | Triennial UST Spill Bucket Integrity Testing (Dri-sump® Test) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - If any periodic test fails, a suspected release report must be submitted on a UST-17A form, UST Suspected Release 24 Hour Notice. The suspected release must be investigated, in accordance with 15A NCAC 2N .0603, and defective equipment repaired or replaced in accordance with 15A NCAC 2N .0404/.0900. Results of the investigation must be submitted on a UST-17B form, UST Suspected Release 7 Day Notice. - Single wall spill buckets not located within a containment sump can use the Dri-sump® testing method. If a spill bucket is located within a containment sump then a hydrostatic or vacuum test would need to be performed on the spill bucket. If the spill bucket is required to be double-walled, then the Dri-sump® testing method can be used to test the containment sump. Complete page 3 of the UST-23B form to document those results. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UST FACILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Owner / Operator Name |  |  |  |  | Facility Name |  |  |  |  | Facility ID#: |  |  |  |  |  |  |  |  |  |
| Facility Street Address |  |  |  |  | Facility City |  |  |  |  | County |  |  |  |  |  |  |  |  |  |
| TESTING CONTRACTOR INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company Name |  |  |  |  | Phone |  |  |  | E-mail Address |  |  |  |  |  |  |  |  |  |  |
|  | I certify, under penalty of law, that the testing data provided on this form documents the UST system equipment was tested in accordance with the manufacturer’s guidelines and the applicable national industry standards listed in 15A NCAC 2N .0406 and/or 15A NCAC 2N .0900, or another method approved by NC DEQ. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Print Name of person conducting test |  |  |  |  |  | Signature of person conducting test |  |  |  |  |  | Test Date |  |  |  |  |  |  |
| Tester Certification #: |  |  |  |  |  | Equipment Certification #: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tester Certification Expiration: |  |  |  |  |  | Equipment Certification Expiration: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Identify Spill Bucket (By Tank Number, Stored Product, etc.) |  |  | Tank # |  | Tank # |  |  | Tank # | Tank # |  |  |  |  | Tank # |  |  |  |  |  |
| Tank Size |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Product |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bucket Manufacturer/Model |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Construction |  |  | SW DW |  | SW DW |  |  | SW DW | SW DW |  |  |  |  | SW DW |  |  |  |  |  |
| Bucket Installation Type |  |  | Direct Bury Direct Bury w/Liner |  | Direct Bury Direct Bury w/Liner |  |  | Direct Bury Direct Bury w/Liner | Direct Bury Direct Bury w/Liner |  |  |  |  | Direct Bury Direct Bury w/Liner |  |  |  |  |  |
| Liquid and debris removed from spill bucket? |  |  | Yes No |  | Yes No |  |  | Yes No | Yes No |  |  |  |  | Yes No |  |  |  |  |  |
| Visual inspection (No cracks, loose parts or separation of the bucket from fill pipe.) |  |  | Pass Fail |  | Pass Fail |  |  | Pass Fail | Pass Fail |  |  |  |  | Pass Fail |  |  |  |  |  |
| VST Communication (Enter VST number) |  |  | VST #: |  | VST #: |  |  | VST #: | VST #: |  |  |  |  | VST #: |  |  |  |  |  |
| Closed Hose (C) (in WC) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Open Hose (O) (in WC) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| VST Connected (V) (in WC) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| VST Communication Passes when: C > O and C > V and V ≥ O |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test length in seconds (DW Primary wall or SW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Laser Verification (DW Primary wall or SW) |  |  | Dot (Pass) Line (Fail) |  | Dot (Pass) Line (Fail) |  |  | Dot (Pass) Line (Fail) | Dot (Pass) Line (Fail) |  |  |  |  | Dot (Pass) Line (Fail) |  |  |  |  |  |
| Test length in seconds (Secondary wall, if DW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Laser Verification (Secondary wall, if DW) |  |  | Dot (Pass) Line (Fail) |  | Dot (Pass) Line (Fail) |  |  | Dot (Pass) Line (Fail) | Dot (Pass) Line (Fail) |  |  |  |  | Dot (Pass) Line (Fail) |  |  |  |  |  |
| Pass/Fail criteria: Must pass visual inspection. Laser result must be a laser-dot (pass). If the first test fails, then conduct a second test entering results in another column. Test is not valid if liquid or debris was not removed from spill bucket. VST location map must be attached to this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Final Test Result |  |  | Pass Fail |  | Pass Fail |  |  | Pass Fail | Pass Fail |  |  |  |  | Pass Fail |  |  |  |  |  |
| Comments – (include information on repairs made prior to testing, and recommended follow-up for failed tests) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date next Spill Bucket integrity test due (required every 3 years) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NORTH CAROLINA DEPARTMENT OF ENVIRONMENTAL QUALITY, DIVISION OF WASTE MANAGEMENT, UST SECTION 1646 MAIL SERVICE CENTER, RALEIGH, NC 27699-1646 PHONE (919) 707-8171 FAX (919) 715-1117 http://www.wastenotnc.org |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11/2022 |  |  |  |

| UST-6D/23A Page 3 |  | Triennial UST Spill Bucket Integrity Testing (DPleak® Test) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - If any periodic test fails, a suspected release report must be submitted on a UST-17A form, UST Suspected Release 24 Hour Notice. The suspected release must be investigated, in accordance with 15A NCAC 2N .0603, and defective equipment repaired or replaced in accordance with 15A NCAC 2N .0404/.0900. Results of the investigation must be submitted on a UST-17B form, UST Suspected Release 7 Day Notice. - Single wall spill buckets not located within a containment sump can use the DPleak® testing method. If a spill bucket is located within a containment sump and is required to be double-walled, then the DPleak® testing method can be used to also test the containment sump. Complete page 4 of the UST-23B form to document those results. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UST FACILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Owner / Operator Name |  |  |  |  |  | Facility Name |  |  |  |  | Facility ID#: |  |  |  |  |  |  |  |  |
| Facility Street Address |  |  |  |  |  | Facility City |  |  |  |  | County |  |  |  |  |  |  |  |  |
| TESTING CONTRACTOR INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company Name |  |  |  |  |  | Phone |  |  |  | E-mail Address |  |  |  |  |  |  |  |  |  |
|  | I certify, under penalty of law, that the testing data provided on this form documents the UST system equipment was tested in accordance with the manufacturer’s guidelines and the applicable national industry standards listed in 15A NCAC 2N .0406 and/or 15A NCAC 2N .0900, or another method approved by NC DEQ. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Print Name of person conducting test |  |  |  |  |  |  | Signature of person conducting test |  |  |  |  |  | Test Date |  |  |  |  |  |
| Tester Certification #: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Identify Spill Bucket (By Tank Number, Stored Product, etc.) |  |  | Tank # |  |  | Tank # |  |  | Tank # | Tank # |  |  |  |  | Tank # |  |  |  |  |
| Tank Size |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Product |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bucket Manufacturer/Model |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Construction |  |  | SW DW |  |  | SW DW |  |  | SW DW | SW DW |  |  |  |  | SW DW |  |  |  |  |
| Bucket Installation Type |  |  | Direct Bury Direct Bury w/Liner |  |  | Direct Bury Direct Bury w/Liner |  |  | Direct Bury Direct Bury w/Liner | Direct Bury Direct Bury w/Liner |  |  |  |  | Direct Bury Direct Bury w/Liner |  |  |  |  |
| Liquid and debris removed from spill bucket? |  |  | Yes No |  |  | Yes No |  |  | Yes No | Yes No |  |  |  |  | Yes No |  |  |  |  |
| Visual inspection (No cracks, loose parts or separation of the bucket from fill pipe.) |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail | Pass Fail |  |  |  |  | Pass Fail |  |  |  |  |
| Wall |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Drain |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Bottom of Riser |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Top of Riser |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Swivel |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Cap |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
|  |  |  | Pass Fail N/A |  |  | Pass Fail N/A |  |  | Pass Fail N/A | Pass Fail N/A |  |  |  |  | Pass Fail N/A |  |  |  |  |
| Pass/Fail criteria: Must pass visual inspection. Test is not valid if liquid or debris was not removed from spill bucket. No areas of spill bucket that fail. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| LDT test report with addendums attached |  |  |  | Yes No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Final Test Result |  |  | Pass Fail |  |  | Pass Fail |  |  | Pass Fail | Pass Fail |  |  |  |  | Pass Fail |  |  |  |  |
| Comments – (include information on repairs made prior to testing, and recommended follow-up for failed tests) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date next Spill Bucket integrity test due (required every 3 years) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NORTH CAROLINA DEPARTMENT OF ENVIRONMENTAL QUALITY, DIVISION OF WASTE MANAGEMENT, UST SECTION 1646 MAIL SERVICE CENTER, RALEIGH, NC 27699-1646 PHONE (919) 707-8171 FAX (919) 715-1117 http://www.wastenotnc.org |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11/2022 |  |  |