| UST-6E/23D |  | Application to Install or Replace Underground Storage Tank Systems (TANK INSTALLATION/TRIENNIAL TESTING) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - A separate form should be used for each facility. If there are more than five (5) tanks at this facility, make additional copies of this page. - The primary and interstitial space of the tank shall be tested in accordance with the manufacturers written guidelines and PEI/RP100 “Recommended Practice for Installation of Underground Liquid Storage Systems.” - The last periodic tightness test record must be maintained by the tank owner or operator and must be readily available for inspection. - Tanks that are not monitored continuously for releases using vacuum, pressure, or hydrostatic methods must be tightness tested at installation, between 6 and 12 months from installation, and every three years following installation. - The interstitial space of the tank shall be tested using a 3rd party certified interstice tightness test capable of detecting a 0.1 gph leak from the inner or outer wall of the interstice for the tank model that is installed. - If the tank fails a tightness test, it must be replaced or repaired by the manufacturer or the manufacturer’s authorized representative in accordance with the manufacturer’s specifications. Following any repair, the tank must be re-tested for tightness. Also a suspected release report must be submitted on a UST-17A form, UST Suspected Release 24 Hour Notice. The suspected release must be investigated, in accordance with 15A NCAC 2N .0603, and any defective equipment repaired/replaced in accordance with 15A NCAC 2N .0404/.0900. Results of the investigation must be submitted on a UST-17B form, UST Suspected Release 7 Day Notice. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UST FACILITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Owner / Operator Name |  |  |  |  |  | Facility Name |  |  |  |  |  |  |  | Facility ID#: |  |  |  |  |  |  |  |  |  |
| Facility Street Address |  |  |  |  |  | Facility City |  |  |  |  |  |  |  | County |  |  |  |  |  |  |  |  |  |
| TESTING CONTRACTOR INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company Name |  |  |  |  |  |  |  |  | Phone |  |  |  |  |  |  | E-mail address |  |  |  |  |  |  |  |
| Mailing Address |  |  |  |  |  |  |  |  | City |  |  |  |  |  |  |  | State |  |  | Zip |  |  |  |
|  | Print Name of person conducting test |  |  |  |  |  |  |  |  |  | Signature of person conducting test |  |  |  |  |  |  |  |  |  |  |  |  |
| Identify Tank (Tank Number, etc.) |  |  | Tank # |  |  |  | Tank # |  |  |  |  | Tank # |  |  | Tank # |  |  |  | Tank # |  |  |  |  |
| Tank Size Product |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UST Type (FRP, Steel Jacketed, Steel/CLAD, Other) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I. Pre-installation testing |  |  |  |  | Vacuum/Pressure Gauge Range (indicate units): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Interstitial space - Liquid Filled or Vacuum |  |  |  |  | Test method: Vacuum Liquid filled/other: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Date |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Test Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Level (liquid) (Indicate units) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Pressure/Vacuum (Indicate units) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Liquid visible on inside/outside of tank (if applicable) |  |  | Yes No |  |  |  | Yes No |  |  |  |  | Yes No |  |  | Yes No |  |  |  | Yes No |  |  |  |  |
| Test Result |  |  | Pass Fail |  |  |  | Pass Fail |  |  |  |  | Pass Fail |  |  | Pass Fail |  |  |  | Pass Fail |  |  |  |  |
| II. Post-installation/triennial testing |  |  |  |  | Tightness Test Model (if applicable): Vacuum/Pressure Gauge Range (indicate units): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Interstitial space - Liquid Filled/Other. |  |  |  |  | Test method: Vacuum Liquid filled/other: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Date: Begin ị End |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Test Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Level (liquid) (Indicate units) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Begin ị End Pressure/Vacuum (Indicate units) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Liquid visible on inside of tank (FRP tanks prior to receiving fuel) |  |  | Yes No N/A |  |  |  | Yes No N/A |  |  |  |  | Yes No N/A |  |  | Yes No N/A |  |  |  | Yes No N/A |  |  |  |  |
| Manufacturer test data sheets attached (e.g., Xerxes Truchek, CSI Standpipe Test) |  |  | Yes N/A |  |  |  | Yes N/A |  |  |  |  | Yes N/A |  |  | Yes N/A |  |  |  | Yes N/A |  |  |  |  |
| Test Result |  |  | Pass Fail |  |  |  | Pass Fail |  |  |  |  | Pass Fail |  |  | Pass Fail |  |  |  | Pass Fail |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NORTH CAROLINA DEPARTMENT OF ENVIRONMENTAL QUALITY, DIVISION OF WASTE MANAGEMENT, UST SECTION 1646 MAIL SERVICE CENTER, RALEIGH, NC 27699-1646 PHONE (919) 707-8171 FAX (919) 715-1117 http://www.wastenotnc.org 11/2022 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |