## Slide 1: Department of Environmental Quality
NC DAQ Public Meeting
Align RNG, LLC – B.F. Grady Rd Proposed Facility
November 16, 2020

## Slide 2: Align RNG, LLC – B.F. Grady Rd Proposed Facility Public Meeting
Department of Environmental Quality
Application for a facility that will process biogas from local farms and inject the methane product into the Natural Gas pipeline for commercial and residential use.
Application Received – 12/10/19
Public Comment Period – May 16- June 15, 2020
Public Comment Period and Public Hearing announced on September 17, 2020

## Slide 3
Iron
Sponge 1
Iron
Sponge 2
Gas upgrading
Bypass valve
Candlestick
Flare (CD-4)
Gas Upgrading
System (GUS)
Tail gas
post GUS
Enclosed
Flare
Product to pipeline
22% Bypassed tail gas
to enclosed flare*
Treated tail gas
to enclosed flare
Enclosed Hybrid flare (CD-3)
emissions to
atmosphere
Off-spec
gas to
candlestick
flare
Biogas feed from
19 on-farm
anaerobic digesters
Must meet NC air toxics and
State SO2 emission standard
78% Tail gas to Iron
Sponge System*
emissions to
atmosphere

## Slide 4: Align RNG, LLC – B.F. Grady Rd Proposed Facility Public Meeting
Department of Environmental Quality
Pollutant | Permitted Potential tons per year
SO2 | 50
NOx | 4.83
CO | 10.10
H2S | 0.49
H2S concentration | 0.35% biogas

## Slide 5
Iron
Sponge 1
Iron
Sponge 2
Gas upgrading
Bypass valve
Candlestick
Flare (CD-4)
(6)
45mmBtu/hr
Pressure Swing
Adsorption
Gas Upgrading
System (GUS)
1200 scfm
Tail gas
post GUS
Max –
233.4 MMSCF/yr
Enclosed
Flare(6)
10mmBtu/hr
Product to pipeline
Max – 397.4 MMscf/yr
22% Bypassed tail gas
to enclosed flare*
Treated tail gas
to enclosed flare
Enclosed Hybrid flare (CD-3)
emissions to
atmosphere
Off-spec
gas to
candlestick
flare
Biogas feed from
19 on-farm
anaerobic digesters –
maximum
630.72 MM scf/yr
All emissions must meet NC air toxics and
State SO2 emission standard
78% Tail gas to Iron
Sponge System*
H2S analyzed quarterly (3)
H2S concentration & flowrate hourly (1,3,4)
Flowrate hourly,
Pressure daily (2)
Pressure daily (2),
H2S ppm every 8 hours (2)
Flowrate calculated hourly (1,3,4)
– Used to demonstrate compliance with 2d .0516 – 2.3 lb/mmbtu – assuming all H2S is oxidized to SO2
-Used to determine Iron Sponge breakthrough – TV avoidance condition
- TV avoidance condition- 12 month rolling total
-2Q .0711 TPER compliance
* Flow percentages at full flow, variable at other rates
Flare combustion efficiency is factored at 100% to maximize potential calculated SO2 emissions and also at 98% to maximize potential calculated H2S emissions
SO2 – mass rate (lb/day) (3) & SO2 lb/mmbtu calculated daily (1)
H2S concentration, Flowrate hourly (3) (1)
Heat sensor continuous (3,4), Natural Gas Flowrate hourly (3)
Heat sensor continuous (1,3,4), Natural Gas Flowrate hourly (1,3)
SO2 – mass rate (lb/day) Calculated daily (3),
H2S calculation when flare used and notification if biogas flared >10hour/day (4)
emissions to
atmosphere
H2S ppm hourly (1,3,4)
Redundant Flow meter
Flowrate hourly when in by-pass (3)
North Carolina – Align Energy RNG BF Grady Rd
Red – measured parameters
Blue – calculated values

## Slide 6: Align RNG, LLC – B.F. Grady Rd Proposed Facility Public Meeting
Dean Carrol
Permit Engineer
NC DAQ – Wilmington Regional Office
Comments may be submitted by email to daq.publiccomments@ncdenr.gov with the subject line “Align Energy.”
Department of Environmental Quality