## Slide 1: Department of Environmental Quality
May 4, 2023
High Rock Lake
Nutrient Management
Wastewater Technical
Advisory Group

## Slide 2: High Rock Lake Nutrient Management Planning Point Source Loading Analysis and Potential Reduction Scenarios Presented to the Wastewater Technical Advisory Group
Bill Kreutzberger
5/4/2023

## Slide 3: Overview of Analysis
Point source summary from modeling documentation
What’s in and not in the watershed model
Estimated 2006 N and P loading – delivered to the lake
Estimated current loading - delivered
P/N reduction curve and potential target adjustments based on uncontrollable sources
Potential reductions from P reduction scenarios
Potential reductions from N reduction scenarios

## Slide 4: High Rock Lake Modeling - Point Sources Documentation, Tetra Tech, 2010
* Inactive permits refers to permits that discharged into the High Rock Lake watershed at some point during the study period, but are currently inactive (no longer discharging).

## Slide 5: Major Dischargers in the Model
NPDES ID | Name | Permitted Flow (mgd) | Comment
NC0004774 | Duke Energy Corp. Buck Steam Station | No limit (cooling water) | Industrial process
NC0004944 | Invista, S.A.R.L. Salisbury Plant | 2.3 | Industrial process
NC0005266 | Louisiana Pacific ABT Co. Mill | 1.0 | Industrial process
NC0005312 | Interface Fabric Elkin, Inc. WWTP | 4.0 | Municipal wastewater
NC0005487 | Color/Tex Finishing Corporation (inactive) | 4.25 | Industrial process
NC0020338 | Town of Yadkinville WWTP | 2.5 | Municipal wastewater
NC0020567 | Town of Elkin WWTP | 1.8 | Municipal wastewater
NC0020591 | City of Statesville Third Creek WWTP | 4.0 | Municipal wastewater
NC0020761 | Town of North Wilkesboro Thurman St WWTP | 2.0 | Municipal wastewater
NC0021121 | City of Mount Airy WWTP | 7.0 | Municipal wastewater
NC0021717 | Town of Wilkesboro Cub Creek WWTP | 4.9 | Municipal wastewater
NC0023884 | Salisbury-Rowan WWTP1 | 20.0 | Municipal wastewater
NC0023884 | City of Salisbury Grants Creek WWTP (inactive)1 | 7.5 | Municipal wastewater
NC0023892 | Town Creek WWTP (inactive)1 | 5.0 | Municipal wastewater
NC0024112 | City of Thomasville Hamby Creek WWTP | 4.0 | Municipal wastewater
NC0024228 | City of High Point Westside WWTP | 6.2 | Municipal wastewater
NC0024872 | Davie County Cooleemee WWTP | 1.5 | Municipal wastewater
NC0026646 | Town of Pilot Mountain WWTP | 1.5 | Municipal wastewater
NC0031836 | City of Statesville Fourth Creek WWTP | 4.0 | Municipal wastewater
NC0037834 | City of Winston-Salem Archie Elledge WWTP | 30.0 | Municipal wastewater
NC0050342 | City of Winston-Salem Muddy Creek WWTP | 21.0 | Municipal wastewater
NC0055786 | City of Lexington WWTP | 5.5 | Municipal wastewater

## Slide 6: Minor Dischargers in the Model
NPDES ID | Name | Permitted Flow (mgd) | Comment
NC0004626 | PPG Industries Fiber Glass – Lexington Facility | 0.60 | Industrial process
NC0005126 | Tyson Foods Inc. Harmony Plant | 0.50 | Industrial process
NC0006548 | Wayne Farms LLC | 0.70 | Industrial process
NC0006696 | Carolina Mirror WWTP (inactive) | 0.5 | Municipal wastewater
NC0020931 | Town of Boonville WWTP | 0.20 | Municipal wastewater
NC0021326 | Town of Dobson WWTP | 0.35 | Municipal wastewater
NC0021491 | Town of Mocksville Dutchmans Creek WWTP | 0.68 | Municipal wastewater
NC0021580 | Town of Jonesville WWTP | 0.40 | Municipal wastewater
NC0025593 | Sowers Ferry Road WWTP (inactive) | 0.75 | Municipal wastewater
NC0029246 | Norfolk Southern Corp-Linwood Yard | 0.32 | Industrial process
NC0049867 | Town of Cleveland WWTP | 0.27 | Municipal wastewater
NC0050903 | Town of Mocksville Bear Creek WWTP | 0.25 | Municipal wastewater
NC0055158 | Bermuda Center Sanitary District WWTP | 0.19 | Municipal wastewater
NC0078361 | Salisbury-Rowan Utilities Second Creek WWTP | 0.09 | Municipal wastewater
NC0079898 | Needmore Rd Landfill (HNA Holdings Inc.) | 0.29 | Groundwater remediation
NC0080853 | Lucent Technologies Salem Business Park Remediation Site | 0.30 | Groundwater remediation
NC0082821 | Southern States Coop-Statesville | 0.14 | Groundwater remediation
NC0083925 | Heater Utilities Inc., Salem Glen SD WWTP | 0.14 | Municipal wastewater

## Slide 7: Point Source Summary
Watershed Model
36 Facilities
Total permitted flow – 137 mgd
Not in Watershed Model
106 facilities
Total permitted flow – 2.36 mgd
  Includes many with no flow limits (cooling water)
  Includes several Water Treatment Plants (backwash)
  Includes numerous schools, small subdivisions, and a few small towns (domestic wastewater)

## Slide 8: Point Source Loading Analysis
Jacobs estimated loads for YPDRBA Members
  2000-2010
2006 Loads
  Used DMR data spreadsheets from DWR
  Where no data – used average flows and concentrations from Tetra Tech memo (small dischargers)
Current Loads
  Used 2019-2022 summary from Jacobs
  Used DMR data from DWR for available years for small dischargers
  Assumed same as 2006 when no more recent data (unless facility known to be inactive/closed)
Delivery factors
  From DWR spreadsheet
  Included factors for dischargers included and not included in the watershed model

## Slide 9: TN and TP Delivery Factors (Portion of load delivered to HRL)

## Slide 10: Summary of Delivered Loads

## Slide 11: Nutrient Reduction Curve
35ug/L seasonal geomean chl-a standard
YAD152C
DRAFT
37% P/50% N reduction equates to a 35ug/L geomean output
42% P/48.5% N reduction equates to 40ug/L at 10% exceedance (statewide standard)
The model cannot predict results accurately from exclusive focus on ONE nutrient and not the other
Therefore, modelers suggest a combination N/P reduction may be preferable for HRL
Standard must be approved by EPA and DWR must make final internal decision about how to proceed based on EPA response
Current N/P

## Slide 12: Impact of Uncontrollable Loads
Steering Committee has yet to make a decision on uncontrollable loads
Assumption - Forested lands, septic systems, and atmospheric loads to water are uncontrollable
  Total Phosphorus
          30% of sources uncontrollable
          P only removal target for all sources of 37% becomes ~53% for controllable sources*
  Total Nitrogen
          29% of sources uncontrollable
          N only removal target for all sources of 50% becomes ~70% for controllable sources*
*These reductions are impacted by Steering Committee decisions and then need to be confirmed by DWR modelers

## Slide 13: Range Finding for Potential TP Reductions

## Slide 14: Range Finding for Potential TN Reductions

## Slide 15: Reduction Targets/Scenarios
Chart: Predicted Phosphorus Reduction % at Technology-based Limits
| 1 mg/L | 0.75 mg/L | 0.5 mg/L
2019-2022 Avg. Flow | 0.69775 | 0.77331 | 0.84888
2019-2022 Avg. +10% | 0.66753 | 0.75064 | 0.83376
Permitted Flow | 0.43732 | 0.57799 | 0.71866

## Slide 16: Reduction Targets/Scenarios
Chart: Predicted Nitrogen Reduction % at Technology-based Limits
| 6 mg/L | 6 or 13 mg/L
2019-2022 Avg. Flow | 0.6305 | 0.59355
2019-2022 Avg. +10% | 0.5806 | 0.53866
Permitted Flow | 0.30011 | 0.15418

## Slide 17: Reduction Proposal
Year 1:
  40+% Phosphorus reduction
Year 5:
  70+% Phosphorus reduction
Year 10:
  10 mg/L Nitrogen limit @ average flow + 10% for all dischargers > 0.1 MGD
  6 mg/L Nitrogen limit @ average flow + 10% for all dischargers > 0.5 MGD

## Slide 18: Discussion

## Slide 19: Rule Elements and Requirements
Allocations and Limits
  Pounds delivered used to calculate NEW total annual mass load allocation (lbs/yr)
  All allocated load is distributed to all dischargers, adjusted by delivery factor
  Permit limits:
    Annual mass limits defined as EOP “equivalent concentration”
    Applied at specified flow, increases with reduced flow
    Limit Options:
      Universal
      Apportioned to be “fair and equitable” – like for like facility load limits based on same EOP concentration
      Only facilities above certain size
    Smaller facility options:
      No limits
      Group annual mass load allocation cap w/ contingency options for exceedance
      Higher EOP limits by facility
  New and expanding dischargers must purchase unused load allocation
    Limits cannot exceed technology-based EOP concentration in rule
Today’s Discussion

## Slide 20: Minimum Discharger Size
Options:
  0.5 MGD
  0.1 MGD
  Other?

## Slide 21: Rule Elements and Requirements
If smaller facilities exceed annual mass load, they must:
  Upgrade treatment to reduce load OR
  Tie into existing facility, allocation transfers to receiving facility
    Combination allocation must be sufficient
Group NPDES Permit:
  If a discharger joins a compliance group, individual limits are superseded by the group allocation sum (i.e. “deemed” compliance)
  Not-for-profit association must apply for group NPDES permit
  If group exceeds allocated annual load, EOP concentration limits apply to all members
  If a discharger leaves the compliance group, EOP concentration limits apply to departing member and original individual allocation follows departing member
  Changes can be made to group permit by minor modification
Limits can be increased only via regionalization

## Slide 22: Rule Elements and Requirements
Trading
  Unused allocation can be bought/sold/leased
  Offsets can be bought or developed in-house:
    Mitigation banks
    In lieu fee
    Credit-generating practices
  Acquired credits/allocation kept in reserve until individual permit modification is obtained and expansion takes place
  Credits are traded based on delivered loads (i.e. more credits necessary as you purchase further upstream)
  Transactions cannot create localized WQ violations

## Slide 23: Annual P Loading by Facility
Chart: 
| 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Lissara WWTP | 9 | 23 | 32 | 110 | 41 | 17 | 32
Dobson WWTP | 108 | 655 | 605 | 696 | 318 | 232 | 890 | 669 | 718 | 980 | 517 | 550 | 406 | 365 | 441 | 370 | 490 | 445 | 289 | 311 | 712 | 959 | 1266 | 1133 | 1526 | 899 | 905 | 415
Boonville WWTP | 229 | 326 | 142 | 422 | 275 | 582 | 1475 | 940 | 1613 | 1077 | 1537 | 589 | 586 | 1261 | 1119 | 3514 | 1187 | 1125 | 984 | 962 | 1071 | 818 | 711 | 664 | 737 | 1099 | 406 | 34
Yadkin Valley Sewer Authority WWTP | 7485 | 6034 | 4237 | 3404 | 5548 | 2817 | 3173 | 2860 | 1968 | 2676 | 2216 | 2668 | 2471 | 2807 | 2949 | 2522 | 2272 | 2359 | 1119 | 771 | 1547 | 664 | 797 | 780 | 1434 | 707 | 918 | 828
Thurman Street WWTP | 3311 | 3093 | 842 | 532 | 1355 | 4179 | 5318 | 4158 | 4834 | 4115 | 4105 | 3797 | 5644 | 4271 | 3735 | 4390 | 4515 | 1809 | 2216 | 2200 | 2060 | 3897 | 4763 | 1710 | 1584 | 2628 | 1696 | 2501
Cooleemee WWTP | 1188 | 2454 | 2904 | 3619 | 2784 | 4197 | 6272 | 5382 | 5723 | 3115 | 2115 | 1970 | 2441 | 2245 | 2529 | 3086 | 3376 | 2654 | 3157 | 6102 | 3840 | 3011 | 4612 | 3990 | 2991 | 2233 | 2759 | 1136
Pilot Mountain WWTP | 13639 | 15343 | 9939 | 9467 | 8045 | 6410 | 5458 | 5739 | 2521 | 3803 | 4076 | 2803 | 3029 | 2883 | 2198 | 2465 | 1970 | 3534 | 2795 | 2199 | 677 | 538 | 818 | 871 | 1292 | 1190 | 1072 | 887
Duvaltex | 43536 | 9963 | 13384 | 15323 | 5105 | 2834 | 4962 | 3022 | 4100 | 6916 | 2619 | 1146 | 1889 | 1701 | 1653 | 879 | 141 | 210 | 266 | 681 | 679 | 901 | 659 | 521 | 743 | 349 | 39 | 2
Yadkinville WWTP | 1538 | 1361 | 1374 | 4712 | 7481 | 7304 | 11580 | 8330 | 6852 | 7595 | 8521 | 9398 | 8613 | 11057 | 9607 | 7677 | 7112 | 9312 | 8604 | 8025 | 8750 | 8454 | 5668 | 5711 | 5527 | 4982 | 3560 | 3559
Hamby Creek WWTP | 26400 | 28364 | 30044 | 26737 | 18636 | 27952 | 29190 | 24232 | 22175 | 16096 | 15708 | 14263 | 19404 | 22517 | 10366 | 2078 | 895 | 887 | 730 | 699 | 585 | 1753
Lexington Regional WWTP | 28106 | 27085 | 27965 | 23081 | 22838 | 20872 | 23830 | 28251 | 26456 | 22193 | 18560 | 3235 | 5364 | 5677 | 5404 | 6850 | 6138 | 4925 | 4678 | 5733 | 4017 | 5086 | 9022 | 5354 | 4009 | 5680 | 9144 | 5743
Westside WWTP | 57802 | 60537 | 62639 | 32937 | 19981 | 12610 | 15637 | 13132 | 15719 | 14276 | 16045 | 8324 | 8737 | 9623 | 7743 | 8091 | 9434 | 7567 | 4871 | 4724 | 7577 | 8359 | 7190 | 3724 | 7191 | 1189 | 2612 | 3027

## Slide 24: Annual N Loading by Facility
Chart: 
| 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Dobson WWTP | 542 | 3851 | 7842 | 2096 | 1039 | 1259 | 1462 | 1388 | 1905 | 3457 | 2699 | 1590 | 2174 | 2175 | 2612 | 3618 | 3750 | 2943 | 2082 | 2878 | 2004 | 2519 | 2273 | 1929 | 3013 | 2263 | 2704 | 2206
Boonville WWTP | 1729 | 1807 | 945 | 1345 | 3623 | 5642 | 3936 | 4239 | 5590 | 3183 | 4617 | 6469 | 7581 | 8526 | 6307 | 6137 | 6130 | 5767 | 4872 | 3983 | 3941 | 1672 | 1882 | 3318 | 176
Yadkin Valley Sewer Authority WWTP | 23865 | 25033 | 14598 | 16978 | 12417 | 9169 | 11095 | 9475 | 9219 | 12324 | 11297 | 10979 | 10610 | 15315 | 13333 | 17243 | 23616 | 23092 | 17565 | 15003 | 18673 | 16020 | 14920 | 14533 | 19067 | 23861 | 18978 | 18228
Thurman Street WWTP | 17262 | 21519 | 6577 | 2376 | 815 | 1710 | 3107 | 16609 | 24876 | 27703 | 13170 | 20510 | 42426 | 25652 | 19719 | 26018 | 18162 | 14594 | 18856 | 31272 | 24590 | 24194 | 34538 | 20803 | 25261 | 26250 | 25244 | 22384
Cooleemee WWTP | 7616 | 21206 | 37761 | 21385 | 21770 | 20673 | 24195 | 23572 | 21879 | 9634 | 14399 | 14322 | 16380 | 10508 | 12754 | 22887 | 28791 | 28081 | 5097 | 15184 | 23602 | 17966 | 20487 | 18131 | 12898 | 14163 | 11664 | 19002
Pilot Mountain WWTP | 31596 | 29250 | 25882 | 28116 | 19722 | 11215 | 28722 | 18636 | 12818 | 11912 | 10053 | 8541 | 10588 | 10131 | 8341 | 8880 | 8767 | 15306 | 9049 | 10044 | 3392 | 3619 | 5968 | 6406 | 5266 | 6797
Duvaltex | 60246 | 23413 | 30733 | 29271 | 36112 | 10582 | 12893 | 11688 | 19073 | 19265 | 15445 | 16865 | 9771 | 8339 | 9981 | 5742
Yadkinville WWTP | 9019 | 7195 | 4902 | 10107 | 22984 | 15210 | 20179 | 16951 | 18507 | 20212 | 37813 | 37486 | 37616 | 34693 | 32737 | 34021 | 33315 | 35495 | 34605 | 37291 | 26899 | 36704 | 33188 | 34790 | 33069 | 33957 | 29135 | 24842
Hamby Creek WWTP | 148123 | 172013 | 194373 | 179662 | 153506 | 186426 | 173398 | 158958 | 157964 | 153067 | 131830 | 138137 | 126294 | 163621 | 70185 | 33115 | 15413 | 24228 | 15802 | 14238 | 23003 | 21002
Lexington Regional WWTP | 192590 | 135527 | 138472 | 165874 | 40151 | 29577 | 45989 | 49626 | 82510 | 126466 | 105948 | 35209 | 28683 | 24789 | 28746 | 44661 | 74142 | 54892 | 30044 | 43182 | 38246 | 38980 | 55180 | 48397 | 50980 | 45763 | 49312 | 22483
Third Creek WWTP | 41392 | 42675 | 42192 | 46987 | 45343 | 46714 | 55182 | 86833 | 80194 | 68548 | 83126 | 68329 | 79536 | 73504 | 69093 | 69186 | 73015 | 49709 | 25244 | 30242 | 37013 | 25372 | 15964 | 17408 | 17434 | 15934 | 22147 | 12749
Fourth Creek WWTP | 90138 | 68365 | 59617 | 74516 | 100734 | 128390 | 66958 | 45429 | 74680 | 76865 | 50369 | 56749 | 52349 | 69784 | 79245 | 66431 | 91998 | 70916 | 50273 | 49353 | 61691 | 47174 | 44172 | 40479 | 49474 | 51542 | 50004 | 45131

## Slide 25: Mean Nitrogen Concentration
By Facility
Chart: 
| 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Archie Elledge WWTP | 11.3135 | 11.0955 | 14.568 | 14.7013 | 15.5906 | 17.0928 | 15.1269 | 15.4426 | 16.3302 | 15.3109 | 15.294 | 14.6445 | 15.7133 | 13.6 | 15.3714 | 16.7
Boonville WWTP | 14.3575 | 14.8477 | 18.7917 | 23.5917 | 18.35 | 18.5525 | 14.1533 | 16.2667 | 18.643 | 21.41 | 16.9988 | 9.19 | 11.576 | 19.254 | 4.6475
Buck Steam Station | 0.8 | 1.15 | 0.98333 | 0.70833 | 0.86667 | 0.79167 | 0.69167 | 0.9 | 1.2154 | 1.5167 | 1.445 | 1.3617 | 1.1192 | 4.8153 | 4.2599 | 4.4294
City of Salisbury WWTP | 21.3992 | 20.4854 | 21.2937 | 21.1923 | 17.8835 | 18.12 | 19.1938 | 17.5694 | 16.6508 | 15.1313 | 16.6481 | 15.7563 | 11.4613 | 10.8333 | 10.2919 | 9.3234
Cooleemee WWTP | 14.0325 | 8.5242 | 8.7475 | 12.8812 | 16.0975 | 18.6083 | 3.4082 | 10.0946 | 14.3708 | 10.8333 | 15.3938 | 12.2658 | 6.9245 | 9.6942 | 7.2042 | 14.0017
Cub Creek WWTP | 30.6833 | 32.7333 | 32.3042 | 23.12 | 28.265 | 35.1 | 27.6333 | 26.1083 | 22.3658 | 25.0908 | 23.4075 | 20.2808 | 14.85 | 13.9175 | 9.0941 | 14.3233
Dobson Plant | 81.859 | 74.4673 | 49.2834 | 60.1487 | 85.325 | 91.3204 | 59.6538 | 71.8057 | 79.35 | 95.9727 | 70.1769 | 48.5808 | 30.275 | 32.4698 | 27.2698 | 27.1788
Dobson WWTP | 4.1858 | 4.1025 | 4.5825 | 6.0525 | 6.4008 | 5.5317 | 4.2473 | 4.7917 | 3.7336 | 4.5808 | 4.1166 | 3.3003 | 4.5692 | 3.34 | 3.8842 | 3.5617
Duvaltex | 3.0314 | 3.2738 | 6.2494 | 7.0583
Fourth Creek WWTP | 6.075 | 7.577 | 8.6008 | 7.1521 | 9.9794 | 10.156 | 7.8715 | 6.8054 | 9.0012 | 7.7287 | 6.4013 | 5.5885 | 5.0583 | 5.0112 | 4.3979 | 4.4734
Hamby Creek WWTP | 15.325 | 21.0717 | 7.7283 | 4.8225 | 1.95 | 3.7508 | 2.3917 | 1.9254 | 2.7958 | 8.465
Lexington Regional WWTP | 3.1008 | 3.6627 | 4.1675 | 4.8233 | 7.6258 | 5.7962 | 3.7308 | 4.7775 | 4.2758 | 4.7908 | 5.9683 | 5.93 | 5.2438 | 4.735 | 5.1208 | 3.615

## Slide 26: Major/Minor Discharge Locations

## Slide 27: Discussion
Department of Environmental Quality
Joey Hester
Joey.hester@ncdenr.gov
O: 919-707-3675
C: 919-418-5712